## Slide 1: Tower configuration
Sensors and Actuators
1 Mechanical level sensor
2 Pressure level sensor
3 Visual level sensor
4 Controlled pump
5 Locations for :
5.1 Flow sensor
5.2 Controlled on/off valve
5.3 Controlled variable valve
6 Location for outlet control valve
(for final competition)
7 Manual valves
(for configuration and test)
∆
0/1
1
2
3
4
5
5
6
7
7
5

## Slide 2: Pump
Commercial aquarium pumps are used. It is possible to adjust somewhat the pump power by using a simple dimmer such as those used for lights.
As these pumps have important internal leakage, a one-way valve has been inserted to avoid reversal of the waterflow when the pump is stopped or runs at low power.
220 V
LED
Optical Fibers
Two different
Pumps are proposed:
Low power pump
Medium power pump
Both use the same control circuitry
Opto-
TRIAC

## Slide 3: Overflow Prevention
To be installed in February 2008

## Slide 4: Mechanical Level Sensor
0-5V
GND
+ 5V
10KΩ
10 turns

## Slide 5: Pressure Level Sensor
Solid state
pressure transducer
0-5V
GND
+ 5V
* 500
P
-2 to 10 mV

## Slide 6: Flow Meter
0/5V
GND
+ 5V
k = 752 pulses / liter
Hall effect
sensor
t
Q = 1/k.t
Instantaneous measurement mode
n pulses
Integrating measurement mode
T
Q = n/k.T

## Slide 7: Waterpeilmeting met Webcam
Water
PC
Webcam
(resolutie 640x480 pixels)
x cm
niveau (n cm)

## Slide 8: Waterpeilmeting met Webcam
Detectie van de overgang tussen lucht en water: discrete gradient magnitude van de pixelwaarde in de y richting (binnen het detectievenster).
480 pixels
Digitaal Beeld afkomstig van de webcam
Detectievenster (manueel instelbaar)
y
pixelwaarde
water
0
480
Lucht/glas
y
0
480
y
Absolute waarde
van de gradient
p pixels
n=p*x/480
p wordt bepaald door te zoeken
naar het maximum van de gradient
magnitude.

## Slide 9: Control System Building Blocks
Bus
master
EIA serial link
Bus
Slave
gp
Fiber optic link
5V sensor
0/1
0/1
Bus
Slave
pc
Fiber optic link
∆
Bus
Slave
pv
∆
Bus
Slave
fm
USB
EIA 485 instrumentation bus
0-5V signal
24V DC control
4-20mA DC control
Pulse frequency

## Slide 10: Bus Master
Interface between PC and EIA485 bus
Personal Computer Interface :
  Serial EIA232 interface at 19200 b/s.
  Data format : 8 bits/char, no parity, one stop bit.
EIA485 bidirectional bus :
  Talk : from master to slave, Red bus led on.
  Listen : from slave to master, Green bus led on.
  Bus reset sequence : 0AH,0DH,0DH,0DH
  Slave command : 0AH, 0DH, Command byte, Data byte.
  Slave answer : 0DH, Slave ID byte, Answer byte.
Display :
  Left display : Command byte
  Right display : Data byte

## Slide 11: Bus Master FSM
State | Description | Bus | Transition Cause | Destination
0 | idle | Tx | Sync_M | 1
1 | Master Initialization, step 1 | Tx | Sync_S # Sync_S | 2 0
2 | Master Initialization, step 2 | Tx | Sync_S # Sync_S | 3 0
3 | Master Initialization, step 3 | Tx | Sync_S # Sync_S | 4 0
4 | End of master Initialization | Tx | Sync_M #(Sync_M and Sync_S) | 5 0
5 | Slave Synchronization | Tx | Sync_S | 6
6 | Slave Receiving Command | Tx | # Sync_S Sync_S | 7 3
7 | Slave Receiving Data | Tx | Any byte | 8
8 | Slave transmitting | Rx | Spontaneous | 9
9 | Wait state | Rx | Sync_M | 5

## Slide 12: Bus Slave Common module
gnd
+5V
Bb
Ba
- 12V
+12V
RA3
RA2
RA0
RA1
- 12V
+12V
gnd
+5V
RA4
RC2
Lsb
msb
Id =
PIC
Slave module V 2.1
1
0
Data
Command

## Slide 13: Bus Slave Common module
Slave Commands : (0AH), 0DH, Command byte, Data Byte.
  Command byte :
    Four msb : Slave ID :
      1 to 14 each ID unique on one bus.
      15 = broadcast
    Four lsb : Command code:
      0 = software reset
      1 to 15 : device specific command.
      Most devices recognize only one command byte
  Data byte :
    Any value between 0 and 255
    Meaning is device specific

## Slide 14: Bus Slave Common module
Slave Answers : 0DH, Slave ID byte, Answer Byte.
  Slave ID byte :
    Four msb : 0000
      Reserved for future developments.
    Four lsb : Slave ID
      Number between 1 and 14.
  Answer byte :
    Any value between 0 and 255
    Meaning is device specific
Broadcast messages are never answered

## Slide 15: Bus Slave Common module
Red LED Display
  Left Display: last Command byte accepted by slave
  Right Display : last Data byte accepted by slave
Green Decimal Display
  Meaning is device specific
  Usually related to the answer byte send by the slave

## Slide 16: General Purpose Interface
Inputs
  0-5 V analog signal between RA0(+) and RA2(ref)
Outputs
  On-off optical command on RA1
  On-off 24 V DC command on RA4
Commands
  0 : software reset
  1 : copy data bits 1 and 4 onto RA ports 1 and 4 and measure input
  2 : measure analog input without affecting digital output
Answer
  Rounded value of 8 most significant bits from AD converter.
Decimal display
  Value of AD input in % of 5 V.
Device ID’s
  First interface = 1; second interface = 9

## Slide 17: AD/DA Interface (not yet available)
Inputs
  0-5 V analog signal with differential buffer
Outputs
  0-5 V buffered analog output, with 1s integrator.
Commands
  0 : software reset
  1 : set analog output signal
Answer
  Rounded value of 8 most significant bits from AD converter.
Decimal display
  Value of AD output in % of 5 V.
Device ID’s
  First interface = 4; second interface = C

## Slide 18: Pump Control
10 mS
10 mS
10 mS
t
t
t

## Slide 19: Pump Control
Inputs
  Optical 50 Hz signal from pump power module
Outputs
  Optical 100 Hz triac firing pulses with adjustable delay after the 50 Hz reference input
Commands
  0 : software reset, switches off the pump.
  3 : sets adjustable delay in the range 0-176 (=B0H) steps of 51μS. The smallest delay results in maximal pump power.
Answer
  Echo of the command data byte.
Decimal display
  Value of firing delay in multiples of 100 μS.
Device ID’s
  First interface = 2, no additional interfaces useful.

## Slide 20: Proportional Valve Control
Inputs
  none
Outputs
  Valve control current, 4-20 mA. Valve is closed at 4 mA.
Commands
  0 : software reset, closes the valve.
  2 : sets valve current in steps of 0.1mA, 0 = 0 mA, .
Answer
  Current through valve before command was received, expressed in multiples of 0.1mA.
Decimal display
  Current in mA.
Device ID’s
  First interface = 2; second interface = 10 (=AH)

## Slide 21: Flow Meter (Version 1.0)
Inputs
  Pulses from Dataflow compact flow transmitter
Outputs
  none
Commands
  0 : software reset.
  4 : request reading of the pulse counter
Answer
  Time interval between successive pulse, in units of 0.4096 mS.
  255 means underflow (out of time range)
Decimal display
  Time interval, expressed in % of 100 mS
Device ID’s
  First interface = 4; second interface = 12 (=CH)

## Slide 22: Flow Meter (Version 2.0, not yet available)
Inputs
  Pulses from Dataflow compact flow transmitter
Outputs
  none
Commands
  0 : software reset.
  4 : data byte = 0:enable pulse duration measurement
  data byte = 1: enable pulse counting measurement
Answer
  Mode 4.0 : pulse duration, in multiples of 0.4096 mS
  Mode 4.1 : Number of pulses in 105 mS.
  In both modes : FFH means “out of range”
Decimal display
  In both modes : Fraction of full range in %
Device ID’s
  First interface = 4; second interface = 12 (=CH)

## Slide 23: Prijslijst
Naam |  | Aantal | Beschikbaar
Small pump | 175 | 3 | 3
Large pump | 225 | 2 | 2
GP Slave Module | 75 * funct | 6 | 6
On-off valve | 60 | 4 | 4
Mech.Level Sensor | 10 | 4 | 4
Pressure Transd 100mb | 75 | 4 | ?
Pressure Transd 10 mb | 150 | 4 | ?
Var Pump Control | 100 | 4 | 4
Var Valve with ctrl | 500 | 3 | 2
Flow meter with ctrl | 215 | 3 | 3
WebCam | 250 | 2 | 1
AD/DA Slave Module + analog | 400 | 4 | 1
Consultant communications | 300 / hour |  | 

## Slide 24: Command Summary
Interface | ID1 | ID2 | CMND | DATA
General Purpose | 1 | 9 | 1,2 | D1= Pump on D4= Valve open
Prop.Valve.Ctrl | 2 | A | 2 | D = 28H = 0 % open D = C8H = 100 % open
Pump control | 3 | - | 3 | D = 08H = max power D > B0H = min power
Flow Meter | 4 | C | 4 | D = 0
(1) Commands with ID = 15 (=FFH) are broadcasts. Slaves don’t generate answers to broadcast messages
(2) Command 0 followed by any data byte resets the interface software and reads the ID switches. No answer is generated.